Finite Element Modeling for  HEAT Transfer of FORCED CONVECTION in INSULATED TUBE With EES Analytical Validation at different Operating conditions

AMR ABBASS

UNED University SPAIN

Abstract

A copper pipe carrying boiling water from the boiler house to the floor above is insulated and sheltered in a duct to avoid exposing the pipe to cold weather. For renovation reasons the pipe’s shelter has been temporarily removed, exposing the pipe to an extreme weather condition. It is critical to the plant operation for the water temperature at the pipe outlet to be maintained above 90oC. The Finite Element Model will be setup in Software Patran and the meshing will be done to execute accurate finite Element Analysis .The Finite Element solution was compared by an EES code in order to demonstrate different operation scenarios.

T1

In Temp of Water

T2

Out Temp of Water

Introduction

The most popular FEA pre- and post-processing software in the world, is Patran offers solid modeling, meshing, analysis setup, and post-processing for a variety of solvers, including MSC Nastran, Patran offers a comprehensive collection of tools that simplify the development of analysis-ready models for thermal, linear, nonlinear, explicit dynamics, and other finite element solutions. Patran makes it simple for anyone to produce FE models, from geometry cleanup tools that help engineers deal with slivers and gaps in CAD to solid modeling tools that allow development of models from scratch. Surfaces and solids can readily be meshed using completely automated meshing processes, manual techniques that offer greater control, or a combination of both. Last but not least, the majority of popular FE solvers have loads, boundary conditions, and analysis setup built in, reducing the need to alter input decks.

In this problem we will Calculate the water temperature at point B under normal working conditions ( Inshelter )

While the pipe is exposed to the extreme weather condition (outside the shelter), we will calculate the water temperate at the pipe outlet TB (at ambient temperature -60 oC)

Use the Patran graphic engine to plot the water temperature from point A to B (X-Y graph)

Use the Patran graphic engine to plot the insulator outside temperature from point C to D (X-Y graph)  and will study the scenario What is the solution if Temperature at outlet at B drops lower than 90 C which is a process limiting factor

Data

- Mass flow rate is 0.04 – 0.16 Kg/m3, currently set to 0.04Kg/m3 to fulfill the plant requirements with the excess amount pumped back to the boiler house

- Normal ambient temperature (inside the shelter) 20oC  Extraordinary ambient temperature (outside the shelter) 40 oC to -60 oC

- Water inlet temperature TA = 100oC

- Water thermal conductivity K = 0.65 W/m0K, mass density 1000 Kg/m3 Water specific heat 𝐶p= 4200 J/Kg. 0K and dynamic viscosity = 0.001 Kg/m.s

- Properties of Material & dimensión of Tube & Insulation

Procedure

- Creat the Geometry of the Model first by making the  Analysis base don model and using “ prefernce to change the global tolerance to 0.0001 to acceot dimensions of 0.0017 mt & above

- Creat one curve with origin as start and [0 0 5] as End

- Creat three Surfaces to represent upper & lower portion of tuve thickness and middle insulation , use Surface XYZ and enter the coordinates as per the geometry

- Creat the material properties for Cu, Insulation and Water

- Creat the Properties of surfaces as Axi Sym  2D element

- Creat properties of Water curve as 1 D flow tube

- Creat the Tria mesh for Surface and bar2 for curve use the mesh seed as indicated in the problem

- Creat the boundary conditions as follows

- Inlet temp ant Node 1 of value 100 C

- Convection on three Surface outside edge   with h=5 W/m0K   and Temp 20 C

- Convection-2 on three surfaces outside edge to represent the  extra ordinary outshelter conditions of h=30 W/mK and T =-60 C

- Coupled  flow convection between the wáter curve 1 and the inside edge of surfaces with mass 0.04 Kg/sec and inlet the K/d*0.023=0.6 and 0.8,0.3 as Re & Pr powers

- Creat the following load Cases

- InShelter with Convection and coupled and inlet Temp as boundary conditions

- Outshelter with convection-2 , coupled and inlet Temp as boundary conditions

- Higher insulation Case with convection 2 but insulation termal conductivity of K=0.1

- Higher mass with convection 2 but mass flow rate 0.16 kg/sec

Steps in Pictures

Fig1-Mesh Seeds

Fig2-Mesh in Tria3 element

Fig3-Mesh in Bar2 Element

Fig4-Coupled Boundary Coditions

Fig5-Convection Boundary Conditions

Fig6-Water Material defnition

Calculations

The inner heat transfer Equation is

Results

A-Inside Shelter

Fig7 Inside the Shelter the tube top  section

Fig8 Inside the Shelter the tube down section

Fig 9 Temperature distribution along water tube axis inside Shelter

Fig 10 Temperature distribution along the outside of Insulation  for tube inside shelter

B-outside Shelter

Fig 11 Outside Shelter tube bottom portion

Fig 12outside shelter Tube Top portion

Fig13 Temperature distribution along water tube axis ouside Shelter

Fig14Temperature distribution along the outside of Insulation outside shelter

Temperature at outlet 90.4 C

Fig 15 Indicate temperature crossed 90c

To accommodate for drop below 90C

- The water  lost heat to outside environment is equal to (Mass X specific heat X Delta T ), so to compensate for more heat transfer due to drop of  outside air  Temperature , we increase the mass flow rate  and it proved to be a solution with extra pumping cost .

Fig 16 Water temp distribution  when mass increased to 0.16 Kg/sec

- The other option but non practical is to use a more resistance Insulator either by increasing Insulator Thickness or using higher resistance material , trailing is the effect of decreasing  the insulation thermal conductivity from 0.33 to 0.1 , this option is not practical

Fig 17 Water temp distribution  when insulation Resistance increased

Analytical solution

A model in Engineering Equation solver was created EES is an iterative software that could solve a group of equations together , the main idea is use and approximation solution by considering the average of  water in and out temperature for heat transfer with Air , the model will give less accurate results but could be used as indication of the main parameters affecting the problem and accordingly utilize FEA analysis of Nastran to get a more accurate results

Program Code

Formatted Equation “ Code in formatted shape”

Parametric table

with different parameters change options , like increasing mass flow rate from 0.04 to 0.16 Kg/Sec and increasing the thickness of insulation or increasing its resistanc

Terms desc.

Thick is thickness of insulation

Tos1 is insulation outer temperature at inlet

Tos2 is insulation outer temperature at exit

T2 is outlet water temp

hout is air outside heat transfer coefficient

Ta is outside air temperature

Conclusion

The Finite Element Model was setup in Patran for the flow across an Insulated Pipe with cold ambient conditions and a design Target to not to exceed 90c and the problem parameters of mass and insulation characteristic was setup the meshing strategy and boundary conditions with executed and the software gave the solution “stable” that exceeded the design parameters different design alternative of mass and insulation increase was introduced to Patran System and the Solution was also validated Analytical through conducting an Analytical Model with Engineering Equation solver .

References

- Introduction to the Finite Element Method by H. Ottosen & N.S. Petersson

- A First Course in Finite Elements by Jacob Fish & Ted Belytschko

- The Finite Element Method: Its Basis and Fundamentals by O. C. Zienkiewicz, R. L. Taylor, J.Z. Zhu

- The Finite Element Method for Engineers by Kenneth H. Huebner, Donald L. Dewhirst, Douglas E. Smith & Ted G. Byrom

- Finite Element Procedures by Klaus-Jürgen Bathe

- MATLAB Guide to Finite Elements: An Interactive Approach by Peter I. Kattan

- The Finite Element Method in Heat Transfer and Fluid Dynamics By J. N. Reddy, D.K. Gartling

- Fundamentals of the Finite Element Method for Heat and Fluid Flow Roland W. Lewis

- Patran Software https://hexagon.com/products/patran

- Engineering equation Solver http://www.fchart.com/ees/

- Engineering Equation Solver manual